COMMUNICATION FLOW in SOLAR PLANTS

String:

A group of solar modules connected in series.

Purpose:

To increase the voltage

Example:

28 modules are connected in series

Each module = 45V

String voltage ~28*45 = 1260V DC

Note:

If one module in series fails badly or is shared, then the whole string output can reduce.

SMB (String Monitoring Box):

Combines multiple strings together.

- Monitors string current

- Provide protection

- Send data to SCADA/PLC

- Inside SMB:

- Fuses

- Surge Protection Device (SPD)

- DC isolator

- Current monitoring cards

- Communication module (RS485/Ethernet)

Example:

1 SMB = 16 strings input

Output goes to inverter

SMB Functions:

- Detect string failure

- Detect low current strings

- Detect blown fuse

- Monitor plant health

BLOCK:

A block is a large section of solar plant.

One block contains:

- Multiple inverters

- Multiple SMB’s

- Thousands of modules

Communication protocols:

| Source | Destination | Protocol |
| --- | --- | --- |
| SMB | PLC | Modbus RTU |
| INVERTER | PLC | Modbus TCP |
| PLC | SCADA | OPC UA/ Modbus TCP |
| SCADA | CLOUD | MQTT/HTTPS |

Example:

16 Strings

↓

1SMB

↓

9SMB’s

↓

1 INVERTER

↓

PLC

↓

SCADA

SCADA (Supervisory Control and Data Acquisition):

- It is a collection both hardware and software components.

- That allows supervision and control of plants both locally and remotely

- The SCADA also examines, collects and processes data in real time

- HMI software facilitates interaction with field devices

Structural Design of Standard SCADA:

Field Devices

↓

RTU / PLC

↓

Communication Network

↓

SCADA Server

↓

HMI / Operator Workstation

Detailed Protocol Flow:

| From | To | Protocol | Medium |
| --- | --- | --- | --- |
| Solar Strings | SMB | Electrical DC | Copper |
| SMB | Inverter | Modbus RTU | RS485 |
| Inverter | PLC/SCADA | Modbus TCP | Ethernet |
| PLC | OPC Server | OPC UA | Ethernet |
| Switch | Control Room (Switch) | TCP/IP | OFC |
| SCADA | Cloud | MQTT/HTTPS | Internet |

- Sensors create data

- PLC collects data

- Switch transfers data

- SCADA displays data

Note:

The WMS system should present with in the 100m distance from the SCADA communication Panel and 70m from the reference cell J-box